## Sheet1
Voltage ratio | 0.00099651 | Vout/Vin | Based on your input voltage divider ratios | [5 empty] | L Line Input Impedance | 1000 | Ohm
Current ratio | 0.014563 | Vout/Ain | Based on your input current shunt/CT ratios | [5 empty] | V Channel Input Impedance | 400 | kOhm
Impulse converter
MMode | [12 empty] | 973 | W
Lgain= | 100: Gain 1 |  |  |  | 100 |  |  |  |  | 1000000000 |  |  | 3.6999 | seconds per impulse | 0.27028 | Hz
Ngain= | 10: Gain 1 |  |  |  | 10 | [7 empty] | 973 | impulses in one hour | 0.21978 | Hz
LNSel= | 1: Meter on L line |  |  |  | 1
DisHPF= | 00: HPF1 and HPF0 |  |  |  | 00
Amod= | 0: Fwd or rev energy pulse output |  |  |  | 0
Rmod= | 0: Fwd or rev reactive energy pulse output |  |  |  | 0
Zxcon= | 10: All zero crossing |  |  |  | 10
Pthresh= | 0010: 3.125% |  |  |  | 0010
Mmode Reg= | 1001010000100010 | [10 empty] | 0.11257
= | 10010100 | 00100010
= | 94 | 22
Mmode Reg= | 0x9422
PL Constant
UN= | 300 | V | Reference voltage, unit is V
Ib= | 12 | A | Basic current, unit is A
GL= | 1 | V/V | L line current circuit gain
VL= | 298.9537 | mV | Sampling voltage of the L line circuit at Ib, unit is mV
VU= | 174.7573 | mV | Sampling voltage of the voltage circuit at UN, unit is mV
MC= | 1000 | imp/kWh | Pulse constant of the energy meter, unit is imp/kWh
PL_Constant= | 12173811
= | 00B9C1F3
PLconstH(0x21)= | 0x00B9
PLconstL(0x22)= | 0xC1F3
Small-Power Mode and Power Offset Compensation
1. Disconnect the current circuit of the energy meter;
2. Write '0xA987' to the SmallPMod register (04H) to enter small-power mode
3. Read out L / N line active / reactive power in small-power mode many times to get a mean value;
4. Write the complement of the above mean value to the corresponding L / N line active / reactive power offset registers;
5. Write any non-0xA987 value to the SmallPMod register (04H) to exit small-power mode
L Line Gain Calibration (Calibrate PL Constant Energy Metering)
L line gain calibration is performed when power factor PF=1.0 and the current is Ib
ETSA Frequency | 0.269 | Hz | Pulse output frequency as measured from ETSA metering using photodiode.
My Frequency | 0.219 | Hz | Pulse output frequency as measured from my energymeter using photodiode.
Error % = | -18.5874 | %
Lratio = | 0.22831 |  |  | 65536 |  | 1010 | 10 | 5
Lgain= | 7481 |  | 58054 |  |  | 0101
Lgain= | 0x1D39
Voltage RMS Gain and L Line Current RMS Gain
Vol_mea= | 203.9 | V | Readout value of the Urms register (49H) | [6 empty] | 0.0077235
Un= | 243.1 | V | Actual Voltage | [6 empty] | 0.24225 | 31.3656
Ugainold= | 26400 |  | 26400 is the default value
= | 31475
Ugain= | 0x7AF3
Cur_meaL= | 19.92 | A | Readout value of the Urms register (49H)
Ib= | 7.74 | A | Actual Voltage
Igainold= | 31251 |  | 31251 is the default value
= | 12142
Igain= | 0x2F6E |  |  | offset=0.003A |  | IgainL | 142
8E
The current offset calibration should be performed at reference voltage and no current.
Calibration is performed by reading the current, multiplying it with the above Igain/2^16 and 2^8,
calculating the complement and writing the result to the L line current offset register (IoffsetL, 35H).
Calibration of voltage offset is similar to that of current offset, but voltage offset
calibration is not applicable for self-powered meter
Voltage Sag Setpoint
Un= | 230 | Nominal voltage
Ugain= | 31475 | From Voltage RMS Gain calc
x%= | 0.94 | 6% below nominal
SagTh = | 7957
SagTh = | 0x1F15
PL_Constant=int(838860800×(G_L×V_L×V_U)/(MC×U_(N`)×I_b ))
U_gain=int((Ugain_old×U_n)/(Vol_mea ))
I_gain=int((Igain_old×I_b)/Cur_mealL )
SagTh=(100×U_n× √2×𝑥%)/(4×𝑈_𝑔𝑎𝑖𝑛/32768)
Note on A5: Wendland, Ryan: L line current gain
Note on A6: Wendland, Ryan: N line current gain
Note on A7: Wendland, Ryan: This bit specifies metering as L line or N line when metering mode is set to flexible mode by MMD1 and MMD0 pins.
Note on A8: Wendland, Ryan: These bits configure the High Pass Filters (HPF) after ADC.
Note on A9: Wendland, Ryan: CF1 output for active power
Note on A10: Wendland, Ryan: CF2 output for reactive power
Note on A11: Wendland, Ryan: These bits configure zero-crossing mode. The ZX pin outputs 5ms-width high level when voltage crosses zero
Note on A12: Wendland, Ryan: These bits configure the L line and N line power difference threshold in anti-tampering mode

## CS1
Reg | Hex Value | H2x | L2x | Decimal H | Decimal L
21 | 00B9 | 00 | B9 | 0 | 185
22 | C1F3 | C1 | F3 | 193 | 243
23 | 1D39 | 1D | 39 | 29 | 57
24 | 0000 | 00 | 00 | 0 | 0
25 | 0000 | 00 | 00 | 0 | 0
26 | 0000 | 00 | 00 | 0 | 0
27 | 08BD | 08 | BD | 8 | 189
28 | 0000 | 00 | 00 | 0 | 0
29 | 0AEC | 0A | EC | 10 | 236
2A | 0000 | 00 | 00 | 0 | 0
2B | 9422 | 94 | 22 | 148 | 34
|  | H2C | L2C
|  | 4A | 34
|  | Reg 2C | 0x4A34
Password | 1234
Ps.: unlock just if necessary
Ps2.: change just the green numbers based on register values

## CS2
Reg | Hex Value | H2x | L2x | Decimal H | Decimal L
31 | D464 | D4 | 64 | 212 | 100
32 | 6E49 | 6E | 49 | 110 | 73
33 | 7530 | 75 | 30 | 117 | 48
34 | 0000 | 00 | 00 | 0 | 0
35 | 0000 | 00 | 00 | 0 | 0
36 | 0000 | 00 | 00 | 0 | 0
37 | 0000 | 00 | 00 | 0 | 0
38 | 0000 | 00 | 00 | 0 | 0
39 | 0000 | 00 | 00 | 0 | 0
3A | 0000 | 00 | 00 | 0 | 0
3B | 0000 | 00 | 00 | 0 | 0
|  | H3C | L3C
|  | D2 | 94
|  | Reg 3C | 0xD294
Password | 1234
Ps.: unlock just if necessary
Ps2.: change just the green numbers based on register values